## Sheet1
SRIDomain | SRIService | Service group | Smart ready service | PartOfMethodA | PartOfMethodB | part of the custom services list?: 1 - YES; 0 - NO | Preconditions | AffectsMaxScore | FunctionalityLevel | FunctionalityDescription | Energy data | Indoor environmental data | Outdoor envionmental data | System and equipment operational data | Control setting and logic data | Occupant data | Desing basis data | Building and system asset data | Utility and grid signal data | Onsite energy generation data | Cyber (IoT) device data | Use Cases
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 | 0 | No automatic control
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 | 1 | Central automatic control
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 | 2 | Individual room control
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 | 3 | Individual room control with communication between controllers and to BACS
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 | 4 | Individual room control with communication and occupancy detection
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 | 0 | No automatic control
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 | 1 | Central automatic control
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 | 2 | Advanced central automatic control
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 | 3 | Advanced central automatic control with intermittent operation and/or room temperature feedback control
Cooling | C-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 0 | Constant temperature control
Cooling | C-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 1 | Outside temperature compensated control
Cooling | C-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 2 | Demand based control
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 0 | No automatic control
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 1 | On off control
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 2 | Multi-Stage control
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 3 | Variable speed pump control (pump unit (internal) estimations)
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 4 | Variable speed pump control (external demand signal)
Cooling | C-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | 0 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 0 | No interlock
Cooling | C-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | 0 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 1 | Partial interlock (minimising risk of simultanieus heating and cooling e.g. by sliding setpoints)
Cooling | C-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | 0 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 2 | Total interlock (control system ensures no simultaneous heating and cooling can take place)
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 | 0 | Continuous storage operation
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 | 1 | Time-scheduled storage operation
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 | 2 | Load prediction based storage operation
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 | 3 | Cold storage capable of flexible control through grid signals (e.g. DSM)
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 0 | On/Off-control of cooling production
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 1 | Multi-stage control of cooling production capacity depending on the load or demand (e.g. on/off of several compressors)
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 2 | Variable control of cooling production capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control)
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 3 | Variable control of cooling production capacity depending on the load AND external signals from grid
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 | 0 | Priorities only based on running times
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 | 1 | Fixed sequencing based on loads only: e.g. depending on the generators characteristics such as absorption chiller vs. centrifugal chiller
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 | 2 | Dynamic priorities based on generator efficiency and characteristics (e.g. availability of free cooling)
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 | 3 | Load prediction based sequencing: the sequence is based on e.g. COP and available power of a device and the predicted required power
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 | 4 | Sequencing based on dynamic priority list, including external signals from grid
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 1 | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage)
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 2 | Central or remote reporting of current performance KPIs and historical data
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 3 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 4 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 0 | No automatic control
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 1 | Scheduled operation of cooling system
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 2 | Self-learning optimal control of cooling system
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 3 | Cooling system capable of flexible control through grid signals (e.g. DSM)
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 4 | Optimized control of cooling system based on local predictions and grid signals (e.g. through model predictive control)
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 0 | No sun shading or only manual operation
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 1 | Motorized operation with manual control
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 2 | Motorized operation with automatic control based on sensor data
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 3 | Combined light/blind/HVAC control
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 4 | Predictive blind control (e.g. based on weather forecast)
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 1 |  |  | 1 | 0 | Manual operation or only fixed windows
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 1 |  |  | 1 | 1 | Open/closed detection to shut down heating or cooling systems
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 1 |  |  | 1 | 2 | Level 1 + Automised mechanical window opening based on room sensor data
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 1 |  |  | 1 | 3 | Level 2 + Centralized coordination of operable windows, e.g. to control free natural night cooling
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 0 | No reporting
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 1 | Position of each product & fault detection
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 2 | Position of each product, fault detection & predictive maintenance
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 3 | Position of each product, fault detection, predictive maintenance, real-time sensor data (wind, lux, temperature…)
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 4 | Position of each product, fault detection, predictive maintenance, real-time & historical sensor data (wind, lux, temperature…)
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 | 0 | Automatic control on / off
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 | 1 | Automatic control on / off and scheduled charging enable
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 | 2 | Automatic control on / off and scheduled charging enable and multi-sensor storage management
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 | 3 | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM)
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 | 0 | Automatic control on / off
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 | 1 | Automatic control on / off and scheduled charging enable
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 | 2 | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 | 3 | DHW production system capable of automatic charging control based on external signals (e.g. from district heating grid)
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 | 0 | Manual selected control of solar energy or heat generation
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 | 1 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 | 2 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 | 3 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 0 | Priorities only based on running time
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 1 | Control according to fixed priority list: e.g. based on rated energy efficiency
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 2 | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels)
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 3 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators)
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 4 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid)
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 |  |  | 1 | 1 | Indication of actual values (e.g. temperatures, submetering energy usage)
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 |  |  | 1 | 2 | Actual values and historical data
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 |  |  | 1 | 3 | Performance evaluation including forecasting and/or benchmarking
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 |  |  | 1 | 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 |  | Only applicable in case of local energy storage | 0 | 1 | Current state of charge (SOC) data available
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 |  | Only applicable in case of local energy storage | 0 | 2 | Actual values and historical data
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 |  | Only applicable in case of local energy storage | 0 | 3 | Performance evaluation including forecasting and/or benchmarking
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 |  | Only applicable in case of local energy storage | 0 | 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 |  | Always to be assessed | 1 | 1 | reporting on current electricity consumption on building level
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 |  | Always to be assessed | 1 | 2 | real-time feedback or benchmarking on building level
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 |  | Always to be assessed | 1 | 3 | real-time feedback or benchmarking on appliance level
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 |  | Always to be assessed | 1 | 4 | real-time feedback or benchmarking on appliance level with automated personalized recommendations
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 1 | Current generation data available
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 2 | Actual values and historical data
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 3 | Performance evaluation including forecasting and/or benchmarking
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 1 | On site storage of electricity (e.g. electric battery)
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 2 | On site storage of energy (e.g. electric battery or thermal storage) with controller based on grid signals
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 3 | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 4 | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity and possibility to feed back into the grid
Electricity | E-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | 0 | 1 |  | Only applicable in case of local energy generation | 0 | 1 | Scheduling electricity consumption (plug loads, white goods, etc.)
Electricity | E-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | 0 | 1 |  | Only applicable in case of local energy generation | 0 | 2 | Automated management of local electricity consumption based on current renewable energy availability
Electricity | E-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | 0 | 1 |  | Only applicable in case of local energy generation | 0 | 3 | Automated management of local electricity consumption based on current and predicted energy needs and renewable energy availability
Electricity | E-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | 0 | 1 |  | Only applicable in case of CHP | 0 | 0 | CHP control based on scheduled runtime management and/or current heat energy demand
Electricity | E-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | 0 | 1 |  | Only applicable in case of CHP | 0 | 1 | CHP runtime control influenced by the fluctuating availability of RES; overproduction will be fed into the grid
Electricity | E-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | 0 | 1 |  | Only applicable in case of CHP | 0 | 2 | CHP runtime control influenced by the fluctuating availability of RES and grid signals; dynamic charging and runtime control to optimise self-consumption of renewables
Electricity | E-8 | DSM- Storage | Support of (micro)grid operation modes | 0 | 1 |  | Only applicable in case of local energy storage | 0 | 1 | Automated management of (building-level) electricity consumption based on grid signals
Electricity | E-8 | DSM- Storage | Support of (micro)grid operation modes | 0 | 1 |  | Only applicable in case of local energy storage | 0 | 2 | Automated management of (building-level) electricity consumption and electricity supply to neighbouring buildings (microgrid) or grid
Electricity | E-8 | DSM- Storage | Support of (micro)grid operation modes | 0 | 1 |  | Only applicable in case of local energy storage | 0 | 3 | Automated management of (building-level) electricity consumption and supply, with potential to continue limited off-grid operation (island mode)
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 | 0 | not present
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 | 1 | ducting (or simple power plug) available
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 | 2 | 0-9% of parking spaces has recharging points
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 | 3 | 10-50% or parking spaces has recharging point
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 | 4 | >50% of parking spaces has recharging point
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | 0 | Not present (uncontrolled charging)
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | 1 | 1-way controlled charging (e.g. including desired departure time and grid signals for optimization)
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | 2 | 2-way controlled charging (e.g. including desired departure time and grid signals for optimization)
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | 0 | No information available
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | 1 | Reporting information on EV charging status to occupant
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | 2 | Reporting information on EV charging status to occupant AND automatic identification and authorizition of the driver to the charging station (ISO 15118 compliant)
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 | 0 | No automatic control
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 | 1 | Central automatic control (e.g. central thermostat)
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 | 2 | Individual room control (e.g. thermostatic valves, or electronic controller)
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 | 3 | Individual room control with communication between controllers and to BACS
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 | 4 | Individual room control with communication and occupancy detection
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 | 0 | No automatic control
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 | 1 | Central automatic control
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 | 2 | Advanced central automatic control
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 | 3 | Advanced central automatic control with intermittent operation and/or room temperature feedback control
Heating | H-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | 1 | 1 |  | Not applicable in case of individual heaters (e.g. stoves) | 0 | 0 | No automatic control
Heating | H-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | 1 | 1 |  | Not applicable in case of individual heaters (e.g. stoves) | 0 | 1 | Outside temperature compensated control
Heating | H-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | 1 | 1 |  | Not applicable in case of individual heaters (e.g. stoves) | 0 | 2 | Demand based control
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 | 0 | No automatic control
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 | 1 | On off control
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 | 2 | Multi-Stage control
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 | 3 | Variable speed pump control (pump unit (internal) estimations)
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 | 4 | Variable speed pump control (external demand signal)
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 | 0 | Continuous storage operation
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 | 1 | Time-scheduled storage operation
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 | 2 | Load prediction based storage operation
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 | 3 | Heat storage capable of flexible control through grid signals (e.g. DSM)
Heating | H-2a | Control heat production facilities | Heat generator control (all except heat pumps) | 1 | 1 |  | Only applicable in case of combustion heater or district heating | 0 | 0 | Constant temperature control
Heating | H-2a | Control heat production facilities | Heat generator control (all except heat pumps) | 1 | 1 |  | Only applicable in case of combustion heater or district heating | 0 | 1 | Variable temperature control depending on outdoor temperature
Heating | H-2a | Control heat production facilities | Heat generator control (all except heat pumps) | 1 | 1 |  | Only applicable in case of combustion heater or district heating | 0 | 2 | Variable temperature control depending on the load (e.g. depending on supply water temperature set point)
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 |  | Only applicable in case of heat pumps | 0 | 0 | On/Off-control of heat generator
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 |  | Only applicable in case of heat pumps | 0 | 1 | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors)
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 |  | Only applicable in case of heat pumps | 0 | 2 | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control)
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 |  | Only applicable in case of heat pumps | 0 | 3 | Variable control of heat generator capacity depending on the load AND external signals from grid
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 0 | Priorities only based on running time
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 1 | Control according to fixed priority list: e.g. based on rated energy efficiency
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 2 | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels)
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 3 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators)
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 4 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid)
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 |  |  | 1 | 1 | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage)
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 |  |  | 1 | 2 | Central or remote reporting of current performance KPIs and historical data
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 |  |  | 1 | 3 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 |  |  | 1 | 4 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 0 | No automatic control
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 1 | Scheduled operation of heating system
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 2 | Self-learning optimal control of heating system
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 3 | Heating system capable of flexible control through grid signals (e.g. DSM)
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 4 | Optimized control of heating system based on local predictions and grid signals (e.g. through model predictive control)
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 |  | Always to be assessed | 1 | 0 | Manual on/off switch
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 |  | Always to be assessed | 1 | 1 | Manual on/off switch + additional sweeping extinction signal
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 |  | Always to be assessed | 1 | 2 | Automatic detection (auto on / dimmed or auto off)
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 |  | Always to be assessed | 1 | 3 | Automatic detection (manual on / dimmed or auto off)
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 | 0 | Manual (central)
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 | 1 | Manual (per room / zone)
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 | 2 | Automatic switching
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 | 3 | Automatic dimming
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 | 4 | Automatic dimming including scene-based light control (during time intervals, dynamic and adapted lighting scenes are set, for example, in terms of illuminance level, different correlated colour temperature (CCT) and the possibility to change the light distribution within the space according to e. g. design, human needs, visual tasks)
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | 1 | 1 |  |  | 1 | 1 | Central or remote reporting of realtime energy use per energy carrier
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | 1 | 1 |  |  | 1 | 2 | Central or remote reporting of realtime energy use per energy carrier, combining TBS of at least 2 domains in one interface
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | 1 | 1 |  |  | 1 | 3 | Central or remote reporting of realtime energy use per energy carrier, combining TBS of all main domains in one interface
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | 1 | 0 | None - No harmonization between grid and TBS; building is operated independently from the grid load
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | 1 | 1 | Demand side management possible for (some) individual TBS, but not coordinated over various domains
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | 1 | 2 | Coordinated demand side management of multiple TBS
Monitoring and control | MC-28 | Feedback - Reporting information | Reporting information regarding demand side management performance and operation | 0 | 1 |  |  | 1 | 1 | Reporting information on current DSM status, including managed energy flows
Monitoring and control | MC-28 | Feedback - Reporting information | Reporting information regarding demand side management performance and operation | 0 | 1 |  |  | 1 | 2 | Reporting information on currenthistorical and predicted DSM status, including managed energy flows
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 | 0 | No DSM control
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 | 1 | DSM control without the possibility to override this control by the building user (occupant or facility manager)
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 | 2 | Manual override and reactivation of DSM control by the building user
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 | 3 | Scheduled override of DSM control (and reactivation) by the building user
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 | 4 | Scheduled override of DSM control and reactivation with optimised control
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | 0 | 1 |  |  | 1 | 0 | Manual setting
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | 0 | 1 |  |  | 1 | 1 | Runtime setting of heating and cooling plants following a predefined time schedule
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | 0 | 1 |  |  | 1 | 2 | Heating and cooling plant on/off control based on building loads
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | 0 | 1 |  |  | 1 | 3 | Heating and cooling plant on/off control based on predictive control or grid signals
Monitoring and control | MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 1 | 1 |  | Always to be assessed | 1 | 1 | Single platform that allows manual control of multiple TBS
Monitoring and control | MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 1 | 1 |  | Always to be assessed | 1 | 2 | Single platform that allows automated control & coordination between TBS
Monitoring and control | MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 1 | 1 |  | Always to be assessed | 1 | 3 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals
Monitoring and control | MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 0 | 1 |  |  | 1 | 0 | No central indication of detected faults and alarms
Monitoring and control | MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 0 | 1 |  |  | 1 | 1 | With central indication of detected faults and alarms for at least 2 relevant TBS
Monitoring and control | MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 0 | 1 |  |  | 1 | 2 | With central indication of detected faults and alarms for all relevant TBS
Monitoring and control | MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 0 | 1 |  |  | 1 | 3 | With central indication of detected faults and alarms for all relevant TBS, including diagnosing functions
Monitoring and control | MC-9 | TBS interaction control | Occupancy detection: connected services | 0 | 1 |  |  | 1 | 1 | Occupancy detection for individual functions, e.g. lighting
Monitoring and control | MC-9 | TBS interaction control | Occupancy detection: connected services | 0 | 1 |  |  | 1 | 2 | Centralised occupant detection which feeds in to several TBS such as lighting and heating
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 | 0 | No ventilation system or manual control
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 | 1 | Clock control
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 | 2 | Occupancy detection control
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 | 3 | Central Demand Control based on air quality sensors (CO2, VOC, humidity, ...)
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 | 4 | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 | 0 | No automatic control: Continuously supplies of air flow for a maximum load of all rooms
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 | 1 | On off time control: Continuously supplies of air flow for a maximum load of all rooms during nominal occupancy time
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 | 2 | Multi-stage control: To reduce the auxiliary energy demand of the fan
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 | 3 | Automatic flow or pressure control without pressure reset: Load dependent supplies of air flow for the demand of all connected rooms.
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 | 4 | Automatic flow or pressure control with pressure reset: Load dependent supplies of air flow for the demand of all connected rooms (for variable air volume systems with VFD).
Ventilation | V-2c | Air temperature control | Heat recovery control: prevention of overheating | 0 | 1 |  | Only in case of mechanical ventilation with heat recovery | 0 | 0 | Without overheating control
Ventilation | V-2c | Air temperature control | Heat recovery control: prevention of overheating | 0 | 1 |  | Only in case of mechanical ventilation with heat recovery | 0 | 1 | Modulate or bypass heat recovery based on sensors in air exhaust
Ventilation | V-2c | Air temperature control | Heat recovery control: prevention of overheating | 0 | 1 |  | Only in case of mechanical ventilation with heat recovery | 0 | 2 | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 | 0 | No automatic control
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 | 1 | Constant setpoint: A control loop enables to control the supply air temperature, the setpoint is constant and can only be modified by a manual action
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 | 2 | Variable set point with outdoor temperature compensation
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 | 3 | Variable set point with load dependant compensation. A control loop enables to control the supply air temperature. The setpoint is defined as a function of the loads in the room
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 | 0 | No automatic control
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 | 1 | Night cooling
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 | 2 | Free cooling: air flows modulated during all periods of time to minimize the amount of mechanical cooling
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 | 3 | H,x- directed control: The amount of outside air and recirculation air are modulated during all periods of time to minimize the amount of mechanical cooling. Calculation is performed on the basis of temperatures and humidity (enthalpy).
Ventilation | V-6 | Feedback - Reporting information | Reporting information regarding IAQ | 1 | 1 |  | Always to be assessed | 1 | 1 | Air quality sensors (e.g. CO2) and real time autonomous monitoring
Ventilation | V-6 | Feedback - Reporting information | Reporting information regarding IAQ | 1 | 1 |  | Always to be assessed | 1 | 2 | Real time monitoring & historical information of IAQ available to occupants
Ventilation | V-6 | Feedback - Reporting information | Reporting information regarding IAQ | 1 | 1 |  | Always to be assessed | 1 | 3 | Real time monitoring & historical information of IAQ available to occupants + warning on maintenance needs or occupant actions (e.g. window opening)