## Sheet1
SRIDomain | SRIService | Service group | Smart ready service | PartOfMethodA | PartOfMethodB | part of the custom services list?: 1 - YES; 0 - NO | Preconditions | AffectsMaxScore | FunctionalityLevel | FunctionalityDescription | Use Cases | Energy data | Indoor environmental data | Outdoor envionmental data | System and equipment operational data | Control setting and logic data | Occupant data | Design basis data | Building and system asset data | Utility and grid signal data | Onsite energy generation data | Cyber (IoT) device data
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 | 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 | 1 | Central automatic control | Demand Management Technologies | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 | 2 | Individual room control | Demand Management Technologies: Smart-zoned residential HVAC control: | electricity: building level: circuit level: battery: fuel: HVAC: | thermal: | thermal: | log: hot water: community level: HVAC: fenestration: System level: | schedule: setpoint: HVAC: | Occupancy: Room Level: | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 | 3 | Individual room control with communication between controllers and to BACS | Demand Management Technologies: Smart-zoned residential HVAC control: | electricity: building level: circuit level: battery: fuel: HVAC: | thermal: | thermal: | log: hot water: community level: HVAC: fenestration: System level: | schedule: setpoint: HVAC: | Occupancy: Room Level: | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 | 4 | Individual room control with communication and occupancy detection | Demand Management Technologies: Smart-zoned residential HVAC control: Occupant count prediction: | electricity: building level: circuit level: battery: fuel: HVAC: | thermal: | thermal: | log: hot water: community level: HVAC: fenestration: System level: | schedule: setpoint: HVAC: | Occupancy: Room Level: | Drawings: | building characteristics: system characteristics: Wifi Location: | Demand response: tariff: | solar: wind: conventional: | proxy (WiFi connection count):
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 | 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 | 1 | Central automatic control | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 | 2 | Advanced central automatic control | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 | 3 | Advanced central automatic control with intermittent operation and/or room temperature feedback control | Demand Management Technologies: Human-Building Interaction | electricity: building level: circuit level: battery: system level: | thermal: air quality: | thermal: | log: hot water: community level: | schedule: setpoint: | occupancy: action: attiude: | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 0 | Constant temperature control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | C-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 1 | Outside temperature compensated control | Sensitivity study on weather data: |  |  | thermal: visual: solar: wind: onsite/local weather station: |  | setpoint: | Occupancy: | Drawings: IEQ criteria: | building characteristics: system characteristics
Cooling | C-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 2 | Demand based control | Sensitivity study on weather data: Demand Management Technologies: | electricity: whole building: circuit level: battery: | thermal: | thermal: visual: solar: wind: onsite/local weather station: | log: hot water: community level: | setpoint: schedule: | Occupancy: | Drawings: IEQ criteria: | building characteristics: system characteristics | Demand response: tariff: | solar: wind: conventional:
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 1 | On off control | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 2 | Multi-Stage control | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 3 | Variable speed pump control (pump unit (internal) estimations) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | 4 | Variable speed pump control (external demand signal) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | 0 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 0 | No interlock | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | C-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | 0 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 1 | Partial interlock (minimising risk of simultanieus heating and cooling e.g. by sliding setpoints) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | 0 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 2 | Total interlock (control system ensures no simultaneous heating and cooling can take place) | Demand Management Technologies: Identification and prevention of energy mismanagement: | electricity: building level: circuit level: battery: fuel: HVAC: Lighting: DHW: Plug-Ins: | thermal: | thermal: | log: hot water: community level: HVAC: fenestration: System level: | schedule: setpoint: HVAC: | Occupancy: Room level: | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 | 0 | Continuous storage operation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 | 1 | Time-scheduled storage operation | Method of generating operational schedule: | electricity: fuel: zone level: | 0 | 0 | 0 | 0 | Occupancy: | Drawings: Rated Power: | building characteristics: system characteristics: | 0 | 0 | 0
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 | 2 | Load prediction based storage operation | Method of generating operational schedule: Development and validation of predictive controls | electricity: fuel: zone level: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: system level: | 0 | Occupancy: | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 | 3 | Cold storage capable of flexible control through grid signals (e.g. DSM) | Method of generating operational schedule: Development and validation of predictive controls | electricity: fuel: zone level: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: system level: | 0 | Occupancy: | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 0 | On/Off-control of cooling production | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 1 | Multi-stage control of cooling production capacity depending on the load or demand (e.g. on/off of several compressors) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 2 | Variable control of cooling production capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 3 | Variable control of cooling production capacity depending on the load AND external signals from grid | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 | 0 | Priorities only based on running times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 | 1 | Fixed sequencing based on loads only: e.g. depending on the generators characteristics such as absorption chiller vs. centrifugal chiller | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 | 2 | Dynamic priorities based on generator efficiency and characteristics (e.g. availability of free cooling) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 | 3 | Load prediction based sequencing: the sequence is based on e.g. COP and available power of a device and the predicted required power | Demand Management Technologies: Development and validation of predictive controls | electricity: building level: circuit level: battery: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: hot water: community level: system level: | schedule: setpoint: | Occupancy: | IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 | 4 | Sequencing based on dynamic priority list, including external signals from grid | Demand Management Technologies: Development and validation of predictive controls | electricity: building level: circuit level: battery: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: hot water: community level: system level: | schedule: setpoint: | Occupancy: | IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 1 | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 2 | Central or remote reporting of current performance KPIs and historical data | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 3 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | System level perfomance: Model validation for aggregated buildings: | electricity: HVAC: lightning: DHW: EV: whole building: | thermal: | thermal: visual: solar: wind: forecast: | HVAC: plant: system level: log: building level: community level: | 0 | Occupancy: | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | 4 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and Fault Detection and Diagnostics | System level perfomance: Model validation for aggregated buildings: Development and validation of predictive controls: Fault Detection and Diagnostics: | electricity: HVAC: lightning: DHW: EV: whole building: fuel: Plug-Ins: | thermal: | thermal: visual: solar: wind: forecast: | HVAC: plant: system level: log: building level: community level: fenestration: | HVAC: setpoint: | Occupancy: room level: | Drawings: IEQ criteria: | building characteristics: system characteristics: | 0 | 0 | 0
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 1 | Scheduled operation of cooling system | Method of generating operational schedule: | electricity: fuel: zone level: | 0 | 0 | 0 | 0 | Occupancy: | Drawings: Rated Power: | building characteristics: system characteristics: | 0 | 0 | 0
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 2 | Self-learning optimal control of cooling system | Method of generating operational schedule: Development and validation of predictive controls | electricity: fuel: zone level: whole building: | thermal | thermal visual: solar: wind: forecast: | log: system level: | 0 | Occupancy: | Drawings: Rated Power: IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 3 | Cooling system capable of flexible control through grid signals (e.g. DSM) | Method of generating operational schedule: Development and validation of predictive controls | electricity: fuel: zone level: whole building: | thermal | thermal visual: solar: wind: forecast: | log: system level: | 0 | Occupancy: | Drawings: Rated Power: IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 4 | Optimized control of cooling system based on local predictions and grid signals (e.g. through model predictive control) | Method of generating operational schedule: Development and validation of predictive controls | electricity: fuel: zone level: whole building: | thermal | thermal visual: solar: wind: forecast: | log: system level: | 0 | Occupancy: | Drawings: Rated Power: IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 0 | No sun shading or only manual operation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 1 | Motorized operation with manual control | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 2 | Motorized operation with automatic control based on sensor data | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 3 | Combined light/blind/HVAC control | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 4 | Predictive blind control (e.g. based on weather forecast) | Demand Management Technologies: Development and validation of model predictive controls | electricity: building level: circuit level: battery: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: hot water: community level: system level: | schedule: setpoint: | Occupancy: | IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 1 |  |  | 1 | 0 | Manual operation or only fixed windows | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 1 |  |  | 1 | 1 | Open/closed detection to shut down heating or cooling systems | Identification and prevention of energy mismanagement: | electricity: fuel: HAC: lightning: DHW: plug-ins: | thermal: | thermal: | HVAC: fenestration: | HVAC: setpoint: | Occupancy: Room Level: | 0 | building characteristics: system characteristics: | 0 | 0 | 0
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 1 |  |  | 1 | 2 | Level 1 + Automised mechanical window opening based on room sensor data | Identification and prevention of energy mismanagement: Smart-zoned residential HVAC control: | electricity: fuel: HAC: lightning: DHW: plug-ins: | thermal: | thermal: | HVAC: fenestration: system level: equipment level: | HVAC: setpoint: | Occupancy: Room Level: | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 1 |  |  | 1 | 3 | Level 2 + Centralized coordination of operable windows, e.g. to control free natural night cooling | Identification and prevention of energy mismanagement: Smart-zoned residential HVAC control: Demand management technologies: | electricity: fuel: HAC: lightning: DHW: plug-ins: whole building: circuit level: battery: | thermal: air quality: | thermal: | HVAC: fenestration: system level: equipment level: log: hot water: community level: | HVAC: setpoint: schedule: | Occupancy: Room Level: | Drawings: | building characteristics: system characteristics: | 0 | solar: wind: conventional: | 0
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 0 | No reporting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 1 | Position of each product & Fault Detection and Diagnostics | Fault Detection and Diagnostics: | electricity: whole building: | thermal: | thermal: | HVAC: plant: system level: equipment level: | HVAC: plant: setpoint: | 0 | 0 | 0 | 0 | 0 | 0
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 2 | Position of each product, Fault Detection and Diagnostics & predictive maintenance | Fault Detection and Diagnostics: | electricity: whole building: | thermal: | thermal: visual: solar: wind: forecast: | HVAC: plant: system level: equipment level: | HVAC: plant: setpoint: | 0 | 0 | 0 | 0 | 0 | 0
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 3 | Position of each product, Fault Detection and Diagnostics, predictive maintenance, real-time sensor data (wind, lux, temperature…) | Fault Detection and Diagnostics: Sensitvity study on weather data: | electricity: whole building: | thermal: | thermal: | HVAC: plant: system level: equipment level: | HVAC: plant: setpoint: | Occupancy: | Drawings: | building characteristics: system characteristics: | 0 | Solar: Wind: | 0
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | 4 | Position of each product, Fault Detection and Diagnostics, predictive maintenance, real-time & historical sensor data (wind, lux, temperature…) | Fault Detection and Diagnostics: Sensitvity study on weather data: | electricity: whole building: | thermal: | thermal: | HVAC: plant: system level: equipment level: | HVAC: plant: setpoint: | Occupancy: | Drawings: | building characteristics: system characteristics: | 0 | Solar: Wind: | 0
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 | 0 | Automatic control on / off | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 | 1 | Automatic control on / off and scheduled charging enable | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 | 2 | Automatic control on / off and scheduled charging enable and multi-sensor storage management | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 | 3 | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 | 0 | Automatic control on / off | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 | 1 | Automatic control on / off and scheduled charging enable | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 | 2 | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 | 3 | DHW production system capable of automatic charging control based on external signals (e.g. from district heating grid) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 | 0 | Manual selected control of solar energy or heat generation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 | 1 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 | 2 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 | 3 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 0 | Priorities only based on running time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 1 | Control according to fixed priority list: e.g. based on rated energy efficiency | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 2 | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 3 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | Demand Management Technologies: Development and validation of predictive controls: | electricity: building level: circuit level: battery: | thermal: | thermal: visual: solar: wind: forecast: | log: hot water: community level: system level: | schedule: setpoint: | Occupancy: | IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 4 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | Demand Management Technologies: Development and validation of predictive controls: | electricity: building level: circuit level: battery: | thermal: | thermal: visual: solar: wind: forecast: | log: hot water: community level: system level: | schedule: setpoint: | Occupancy: | IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 |  |  | 1 | 1 | Indication of actual values (e.g. temperatures, submetering energy usage) | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 |  |  | 1 | 2 | Actual values and historical data | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 |  |  | 1 | 3 | Performance evaluation including forecasting and/or benchmarking | System level perfomance: Model validation for aggregated buildings: | electricity: HVAC: lightning: DHW: EV: whole building: | thermal: | thermal: visual: solar: wind: forecast: | HVAC: plant: system level: log: building level: community level: | 0 | Occupancy: | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 |  |  | 1 | 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and Fault Detection and Diagnostics | System level perfomance: Model validation for aggregated buildings: Development and validation of predictive controls: Fault Detection and Diagnostics: | electricity: HVAC: lightning: DHW: EV: whole building: fuel: Plug-Ins: | thermal: | thermal: visual: solar: wind: forecast: | HVAC: plant: system level: log: building level: community level: fenestration: | HVAC: setpoint: | Occupancy: room level: | Drawings: IEQ criteria: | building characteristics: system characteristics: | 0 | 0 | 0
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 |  | Only applicable in case of local energy storage | 0 | 1 | Current state of charge (SOC) data available | ?
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 |  | Only applicable in case of local energy storage | 0 | 2 | Actual values and historical data | ?
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 |  | Only applicable in case of local energy storage | 0 | 3 | Performance evaluation including forecasting and/or benchmarking | ?
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 |  | Only applicable in case of local energy storage | 0 | 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and Fault Detection and Diagnostics | Development and validation of predictive controls: Fault Detection and Diagnostics: | electricity: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: system level: | 0 | Occupany: | IEQ criteria: | building characteristics: system characteristics: | 0 | 0 | 0
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 |  | Always to be assessed | 1 | 1 | reporting on current electricity consumption on building level | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 |  | Always to be assessed | 1 | 2 | real-time feedback or benchmarking on building level | System level perfomance: Human-Building Interaction: | electricity: HVAC: lightning: DHW: EV: fuel: building level: system level: | thermal: air quality: | 0 | HVAC: plant: system level: | 0 | occupancy: action: attiude: | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 |  | Always to be assessed | 1 | 3 | real-time feedback or benchmarking on appliance level | System level perfomance: Human-Building Interaction: | electricity: HVAC: lightning: DHW: EV: fuel: building level: system level: | thermal: air quality: | 0 | HVAC: plant: system level: | 0 | occupancy: action: attiude: | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 |  | Always to be assessed | 1 | 4 | real-time feedback or benchmarking on appliance level with automated personalized recommendations | System level perfomance: Human-Building Interaction: | electricity: HVAC: lightning: DHW: EV: fuel: building level: system level: | thermal: air quality: | 0 | HVAC: plant: system level: | 0 | occupancy: action: attiude: | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 1 | Current generation data available | Sensitivity study on weather data: | 0 | 0 | thermal: visual: solar: wind: onsite/local weather station: | 0 | setpoint: | Occupancy: | Drawings: IEQ criteria: | building characteristics: system characteristics | 0 | 0 | 0
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 2 | Actual values and historical data | Sensitivity study on weather data: | 0 | 0 | thermal: visual: solar: wind: onsite/local weather station: | 0 | setpoint: | Occupancy: | Drawings: IEQ criteria: | building characteristics: system characteristics | 0 | 0 | 0
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 3 | Performance evaluation including forecasting and/or benchmarking | Sensitivity study on weather data: Model validation for aggregated buildings: | electricity: whole building: | 0 | thermal: visual: solar: wind: onsite/local weather station: forecast: | log: building level: community level: | setpoint: | Occupancy: | Drawings: IEQ criteria: | building characteristics: system characteristics | tariff: | solar: wind: conventional: | 0
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and Fault Detection and Diagnostics | Sensitivity study on weather data: Model validation for aggregated buildings: Development and validation of predictive controls: Fault Detection and Diagnostics and Diagnostics: | electricity: whole building: fuel: HVAC: Lighting: DHW: Plug-ins: | thermal | thermal: visual: solar: wind: onsite/local weather station: forecast: | log: building level: community level: system level: HVAC: fenestration: | setpoint: HVAC: | Occupancy: Room Level: | Drawings: IEQ criteria: | building characteristics: system characteristics | tariff: | solar: wind: conventional: | 0
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 1 | On site storage of electricity (e.g. electric battery) | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 2 | On site storage of energy (e.g. electric battery or thermal storage) with controller based on grid signals | System level perfomance: Demand Management Technologies: | electricity: HVAC: lightning: DHW: EV: whole building: circuit level: battery: | thermal: | thermal: | HVAC: plant: system level: log: hot water: community level: | schedule: setpoint: | 0 | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 3 | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity | System level perfomance: Demand Management Technologies: Development and validation of predictive controls | electricity: HVAC: lightning: DHW: EV: whole building: circuit level: battery: | thermal: | thermal: visual: solar: wind: forecast: | HVAC: plant: system level: log: hot water: community level: | schedule: setpoint: | 0 | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 |  | Only applicable in case of local energy generation | 0 | 4 | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity and possibility to feed back into the grid | System level perfomance: Demand Management Technologies: Development and validation of predictive controls | electricity: HVAC: lightning: DHW: EV: whole building: circuit level: battery: | thermal: | thermal: visual: solar: wind: forecast: | HVAC: plant: system level: log: hot water: community level: | schedule: setpoint: | 0 | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Electricity | E-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | 0 | 1 |  | Only applicable in case of local energy generation | 0 | 1 | Scheduling electricity consumption (plug loads, white goods, etc.) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Electricity | E-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | 0 | 1 |  | Only applicable in case of local energy generation | 0 | 2 | Automated management of local electricity consumption based on current renewable energy availability | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Electricity | E-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | 0 | 1 |  | Only applicable in case of local energy generation | 0 | 3 | Automated management of local electricity consumption based on current and predicted energy needs and renewable energy availability | Demand Management Technologies: Development and validation of predictive controls | electricity: building level: circuit level: battery: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: hot water: community level: system level: | schedule: setpoint: | Occupancy: | IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Electricity | E-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | 0 | 1 |  | Only applicable in case of CHP | 0 | 0 | CHP control based on scheduled runtime management and/or current heat energy demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electricity | E-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | 0 | 1 |  | Only applicable in case of CHP | 0 | 1 | CHP runtime control influenced by the fluctuating availability of RES; overproduction will be fed into the grid | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Electricity | E-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | 0 | 1 |  | Only applicable in case of CHP | 0 | 2 | CHP runtime control influenced by the fluctuating availability of RES and grid signals; dynamic charging and runtime control to optimise self-consumption of renewables | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Electricity | E-8 | DSM- Storage | Support of (micro)grid operation modes | 0 | 1 |  | Only applicable in case of local energy storage | 0 | 1 | Automated management of (building-level) electricity consumption based on grid signals | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Electricity | E-8 | DSM- Storage | Support of (micro)grid operation modes | 0 | 1 |  | Only applicable in case of local energy storage | 0 | 2 | Automated management of (building-level) electricity consumption and electricity supply to neighbouring buildings (microgrid) or grid | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Electricity | E-8 | DSM- Storage | Support of (micro)grid operation modes | 0 | 1 |  | Only applicable in case of local energy storage | 0 | 3 | Automated management of (building-level) electricity consumption and supply, with potential to continue limited off-grid operation (island mode) | Demand Management Technologies: Development and validation of predictive controls: | electricity: building level: circuit level: battery: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: hot water: community level: system level: | schedule: setpoint: | Occupancy: | IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 | 0 | not present | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 | 1 | ducting (or simple power plug) available | ?
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 | 2 | 0-9% of parking spaces has recharging points | ?
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 | 3 | 10-50% or parking spaces has recharging point | ?
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 | 4 | >50% of parking spaces has recharging point | ?
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | 0 | Not present (uncontrolled charging) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | 1 | 1-way controlled charging (e.g. including desired departure time and grid signals for optimization) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | 2 | 2-way controlled charging (e.g. including desired departure time and grid signals for optimization) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | 0 | No information available | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | 1 | Reporting information on EV charging status to occupant | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | 2 | Reporting information on EV charging status to occupant AND automatic identification and authorizition of the driver to the charging station (ISO 15118 compliant) | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 | 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 | 1 | Central automatic control (e.g. central thermostat) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 | 3 | Individual room control with communication between controllers and to BACS | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 | 4 | Individual room control with communication and occupancy detection | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 | 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 | 1 | Central automatic control | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 | 2 | Advanced central automatic control | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 | 3 | Advanced central automatic control with intermittent operation and/or room temperature feedback control | Demand Management Technologies: Human-Building Interaction: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | 1 | 1 |  | Not applicable in case of individual heaters (e.g. stoves) | 0 | 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | H-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | 1 | 1 |  | Not applicable in case of individual heaters (e.g. stoves) | 0 | 1 | Outside temperature compensated control | Sensitivity study on weather data: | 0 | 0 | thermal: visual: solar: wind: onsite/local weather station: |  | setpoint: | Occupancy: | Drawings: IEQ criteria: | building characteristics: system characteristics | 0 | 0 | 0
Heating | H-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | 1 | 1 |  | Not applicable in case of individual heaters (e.g. stoves) | 0 | 2 | Demand based control | Sensitivity study on weather data: Demand Management Technologies: | electricity: whole building: circuit level: battery: | thermal: | thermal: visual: solar: wind: onsite/local weather station: | log: hot water: community level: | setpoint: schedule: | Occupancy: | Drawings: IEQ criteria: | building characteristics: system characteristics | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 | 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 | 1 | On off control | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 | 2 | Multi-Stage control | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 | 3 | Variable speed pump control (pump unit (internal) estimations) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 | 4 | Variable speed pump control (external demand signal) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 | 0 | Continuous storage operation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 | 1 | Time-scheduled storage operation | Method of generating operational schedule: | electricity: fuel: zone level: | 0 | 0 | 0 | 0 | Occupancy: | Drawings: Rated Power: | building characteristics: system characteristics: | 0 | 0 | 0
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 | 2 | Load prediction based storage operation | Method of generating operational schedule: Development and validation of predictive controls: | electricity: fuel: zone level: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: system level: | 0 | Occupancy: | Drawings: Rated Power: | building characteristics: system characteristics: | 0 | 0 | 0
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 | 3 | Heat storage capable of flexible control through grid signals (e.g. DSM) | Method of generating operational schedule: Development and validation of predictive controls: | electricity: fuel: zone level: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: system level: | 0 | Occupancy: | Drawings: Rated Power: | building characteristics: system characteristics: | 0 | 0 | 0
Heating | H-2a | Control heat production facilities | Heat generator control (all except heat pumps) | 1 | 1 |  | Only applicable in case of combustion heater or district heating | 0 | 0 | Constant temperature control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | H-2a | Control heat production facilities | Heat generator control (all except heat pumps) | 1 | 1 |  | Only applicable in case of combustion heater or district heating | 0 | 1 | Variable temperature control depending on outdoor temperature | Sensitivity study on weather data: | 0 | 0 | thermal: visual: solar: wind: onsite/local weather station: | 0 | setpoint: | Occupancy: | Drawings: IEQ criteria: | building characteristics: system characteristics | 0 | 0 | 0
Heating | H-2a | Control heat production facilities | Heat generator control (all except heat pumps) | 1 | 1 |  | Only applicable in case of combustion heater or district heating | 0 | 2 | Variable temperature control depending on the load (e.g. depending on supply water temperature set point) | Sensitivity study on weather data: Demand Management Technologies: | electricity: whole building: circuit level: battery: | thermal: | thermal: visual: solar: wind: onsite/local weather station: | log: hot water: community level: | setpoint: schedule: | Occupancy: | Drawings: IEQ criteria: | building characteristics: system characteristics | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 |  | Only applicable in case of heat pumps | 0 | 0 | On/Off-control of heat generator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 |  | Only applicable in case of heat pumps | 0 | 1 | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 |  | Only applicable in case of heat pumps | 0 | 2 | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 |  | Only applicable in case of heat pumps | 0 | 3 | Variable control of heat generator capacity depending on the load AND external signals from grid | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 0 | Priorities only based on running time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 1 | Control according to fixed priority list: e.g. based on rated energy efficiency | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 2 | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 3 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators) | Demand Management Technologies: Development and validation of predicted controls | electricity: building level: circuit level: battery: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: hot water: community level: system level: | schedule: setpoint: | Occupancy: | IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | 4 | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid) | Demand Management Technologies: Development and validation of predicted controls | electricity: building level: circuit level: battery: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: hot water: community level: system level: | schedule: setpoint: | Occupancy: | IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 |  |  | 1 | 1 | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage) | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 |  |  | 1 | 2 | Central or remote reporting of current performance KPIs and historical data | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 |  |  | 1 | 3 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking | System level perfomance: Model validation for aggregated buildings: | electricity: HVAC: lightning: DHW: EV: whole building: | thermal: | thermal: visual: solar: wind: forecast: | HVAC: plant: system level: log: building level_ community level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | tariff: | solar: wind: conventional: | 0
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 |  |  | 1 | 4 | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and Fault Detection and Diagnostics | System level perfomance: Model validation for aggregated buildings: Development and validation of predctive controls: | electricity: HVAC: lightning: DHW: EV: whole building: | thermal: | thermal: visual: solar: wind: forecast: | HVAC: plant: system level: log: building level_ community level: | 0 | Occupancy: | Drawings: IEQ criteria: | building characteristics: system characteristics: | tariff: | solar: wind: conventional: | 0
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 1 | Scheduled operation of heating system | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 2 | Self-learning optimal control of heating system | Demand Management Technologies: Development and validation of predictive controls: | electricity: building level: circuit level: battery: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: hot water: community level: system level: | schedule: setpoint: | Occupancy: | IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 3 | Heating system capable of flexible control through grid signals (e.g. DSM) | Demand Management Technologies: Development and validation of predictive controls: | electricity: building level: circuit level: battery: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: hot water: community level: system level: | schedule: setpoint: | Occupancy: | IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | 4 | Optimized control of heating system based on local predictions and grid signals (e.g. through model predictive control) | Demand Management Technologies: Development and validation of predictive controls: | electricity: building level: circuit level: battery: whole building: | thermal: | thermal: visual: solar: wind: forecast: | log: hot water: community level: system level: | schedule: setpoint: | Occupancy: | IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 |  | Always to be assessed | 1 | 0 | Manual on/off switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 |  | Always to be assessed | 1 | 1 | Manual on/off switch + additional sweeping extinction signal | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 |  | Always to be assessed | 1 | 2 | Automatic detection (auto on / dimmed or auto off) | Demand Management Technologies: Occupant Count Prediction: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | Occupancy: | 0 | building characteristics: system characteristics: wifi location: | Demand response: tariff: | solar: wind: conventional: | proxy (WiFi connection count):
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 |  | Always to be assessed | 1 | 3 | Automatic detection (manual on / dimmed or auto off) | Demand Management Technologies: Occupant Count Prediction: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | Occupancy: | 0 | building characteristics: system characteristics: wifi location: | Demand response: tariff: | solar: wind: conventional: | proxy (WiFi connection count):
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 | 0 | Manual (central) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 | 1 | Manual (per room / zone) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 | 2 | Automatic switching | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 | 3 | Automatic dimming | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 | 4 | Automatic dimming including scene-based light control (during time intervals, dynamic and adapted lighting scenes are set, for example, in terms of illuminance level, different correlated colour temperature (CCT) and the possibility to change the light distribution within the space according to e. g. design, human needs, visual tasks) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | 1 | 1 |  |  | 1 | 1 | Central or remote reporting of realtime energy use per energy carrier | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | 1 | 1 |  |  | 1 | 2 | Central or remote reporting of realtime energy use per energy carrier, combining TBS of at least 2 domains in one interface | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | 1 | 1 |  |  | 1 | 3 | Central or remote reporting of realtime energy use per energy carrier, combining TBS of all main domains in one interface | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | 1 | 0 | None - No harmonization between grid and TBS; building is operated independently from the grid load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | 1 | 1 | Demand side management possible for (some) individual TBS, but not coordinated over various domains | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | 1 | 2 | Coordinated demand side management of multiple TBS | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-28 | Feedback - Reporting information | Reporting information regarding demand side management performance and operation | 0 | 1 |  |  | 1 | 1 | Reporting information on current DSM status, including managed energy flows | Demand Management Technologies: System level perfomance: | electricity: building level: circuit level: battery: HVAC: lightning: DHW: EV | thermal: | thermal: | log: hot water: community level: HVAC: plant: system level: | schedule: setpoint: | 0 | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-28 | Feedback - Reporting information | Reporting information regarding demand side management performance and operation | 0 | 1 |  |  | 1 | 2 | Reporting information on currenthistorical and predicted DSM status, including managed energy flows | Demand Management Technologies: System level perfomance: | electricity: building level: circuit level: battery: HVAC: lightning: DHW: EV | thermal: | thermal: | log: hot water: community level: HVAC: plant: system level: | schedule: setpoint: | 0 | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 | 0 | No DSM control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 | 1 | DSM control without the possibility to override this control by the building user (occupant or facility manager) | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 | 2 | Manual override and reactivation of DSM control by the building user | Demand Management Technologies: Human-Building Interaction | electricity: building level: circuit level: battery: fuel: system level: | thermal: air quality: | thermal: visual: solar: wind: | log: hot water: community level: HVAC: | schedule: setpoint: | occupancy: Actions: attitude | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 | 3 | Scheduled override of DSM control (and reactivation) by the building user | Demand Management Technologies: Human-Building Interaction | electricity: building level: circuit level: battery: fuel: system level: | thermal: air quality: | thermal: visual: solar: wind: | log: hot water: community level: HVAC: | schedule: setpoint: | occupancy: Actions: attitude | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 | 4 | Scheduled override of DSM control and reactivation with optimised control | Demand Management Technologies: Human-Building Interaction: Development and validation of predictive controls: | electricity: building level: circuit level: battery: fuel: system level: | thermal: air quality: | thermal: visual: solar: wind: forecast: | log: hot water: community level: HVAC: system level: | schedule: setpoint: | occupancy: Actions: attitude | Drawings: IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | 0 | 1 |  |  | 1 | 0 | Manual setting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | 0 | 1 |  |  | 1 | 1 | Runtime setting of heating and cooling plants following a predefined time schedule | Method of generating operational schedule: | electricity: fuel: zone level: | 0 | 0 | 0 | 0 | Occupancy: | Drawings: Rated Power: | building characteristics: system characteristics: | 0 | 0 | 0
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | 0 | 1 |  |  | 1 | 2 | Heating and cooling plant on/off control based on building loads | Method of generating operational schedule: Demand Management Technologies: | electricity: fuel: zone level: whole building: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | Occupancy: | Drawings: Rated Power: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | 0 | 1 |  |  | 1 | 3 | Heating and cooling plant on/off control based on predictive control or grid signals | Method of generating operational schedule: Demand Management Technologies: | electricity: fuel: zone level: whole building: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | Occupancy: | Drawings: Rated Power: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 1 | 1 |  | Always to be assessed | 1 | 1 | Single platform that allows manual control of multiple TBS | System level perfomance: Demand Management Technologies: | electricity: HVAC: lightning: DHW: EV: whole building: circuit level: battery: | thermal: | thermal: | HVAC: plant: system level: log: hot water: community level: | schedule: setpoint: | 0 | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 1 | 1 |  | Always to be assessed | 1 | 2 | Single platform that allows automated control & coordination between TBS | System level perfomance: Demand Management Technologies: | electricity: HVAC: lightning: DHW: EV: whole building: circuit level: battery: | thermal: | thermal: | HVAC: plant: system level: log: hot water: community level: | schedule: setpoint: | 0 | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 1 | 1 |  | Always to be assessed | 1 | 3 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | System level perfomance: Demand Management Technologies: Development and validation of predictive controls: | electricity: HVAC: lightning: DHW: EV: whole building: circuit level: battery: | thermal: | thermal: visual: solar: wind: forecast: | HVAC: plant: system level: log: hot water: community level: | schedule: setpoint: | Occupancy: | Drawings: IEQ criteria: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Monitoring and control | MC-4 | Fault Detection and Diagnostics | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 0 | 1 |  |  | 1 | 0 | No central indication of detected faults and alarms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monitoring and control | MC-4 | Fault Detection and Diagnostics | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 0 | 1 |  |  | 1 | 1 | With central indication of detected faults and alarms for at least 2 relevant TBS | Fault Detection and Diagnostics: | electricity: whole building: | thermal: | thermal: | HVAC: plant: system level: equipment level: | HVAC: plant: setpoint: | 0 | 0 | 0 | 0 | 0 | 0
Monitoring and control | MC-4 | Fault Detection and Diagnostics | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 0 | 1 |  |  | 1 | 2 | With central indication of detected faults and alarms for all relevant TBS | Fault Detection and Diagnostics: | electricity: whole building: | thermal: | thermal: | HVAC: plant: system level: equipment level: | HVAC: plant: setpoint: | 0 | 0 | 0 | 0 | 0 | 0
Monitoring and control | MC-4 | Fault Detection and Diagnostics | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 0 | 1 |  |  | 1 | 3 | With central indication of detected faults and alarms for all relevant TBS, including diagnosing functions | Fault Detection and Diagnostics: | electricity: whole building: | thermal: | thermal: | HVAC: plant: system level: equipment level: | HVAC: plant: setpoint: | 0 | 0 | 0 | 0 | 0 | 0
Monitoring and control | MC-9 | TBS interaction control | Occupancy detection: connected services | 0 | 1 |  |  | 1 | 1 | Occupancy detection for individual functions, e.g. lighting | Occupant Count Prediction: | 0 | 0 | 0 | 0 | 0 | Occupancy: | 0 | system characteristics (with location): | 0 | 0 | proxy (WiFi connection count):
Monitoring and control | MC-9 | TBS interaction control | Occupancy detection: connected services | 0 | 1 |  |  | 1 | 2 | Centralised occupant detection which feeds in to several TBS such as lighting and heating | Occupant Count Prediction: | 0 | 0 | 0 | 0 | 0 | Occupancy: | 0 | system characteristics (with location): | 0 | 0 | proxy (WiFi connection count):
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 | 0 | No ventilation system or manual control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 | 1 | Clock control | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 | 2 | Occupancy detection control | Demand Management Technologies: Occupant Count prediction | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | Occupancy: | 0 | building characteristics: system characteristics: system chrachtericists (wifi location): | Demand response: tariff: | solar: wind: conventional: | proxy (WiFi connection count):
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 | 3 | Central Demand Control based on air quality sensors (CO2, VOC, humidity, ...) | Demand Management Technologies: Occupant Count prediction: Co-Optimizing IEQ and energy: | electricity: building level: circuit level: battery: HVAC: system level: | thermal: visual: air quality: acoustic: | thermal: solar: wind: air quality: | log: hot water: community level: HVC: zone level: | schedule: setpoint: HVAC: | Occupancy: zone level: | 0 | building characteristics: system characteristics: system chrachtericists (wifi location): | Demand response: tariff: | solar: wind: conventional: | proxy (WiFi connection count):
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 | 4 | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers | Demand Management Technologies: Occupant Count prediction: Co-Optimizing IEQ and energy: | electricity: building level: circuit level: battery: HVAC: system level: | thermal: visual: air quality: acoustic: | thermal: solar: wind: air quality: | log: hot water: community level: HVC: zone level: | schedule: setpoint: HVAC: | Occupancy: zone level: | 0 | building characteristics: system characteristics: system chrachtericists (wifi location): | Demand response: tariff: | solar: wind: conventional: | proxy (WiFi connection count):
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 | 0 | No automatic control: Continuously supplies of air flow for a maximum load of all rooms | 0
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 | 1 | On off time control: Continuously supplies of air flow for a maximum load of all rooms during nominal occupancy time | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 | 2 | Multi-stage control: To reduce the auxiliary energy demand of the fan | Demand Management Technologies: Occupant Count Prediction: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | Occupancy: | 0 | building characteristics: system characteristics: system chrachtericists (wifi location): | Demand response: tariff: | solar: wind: conventional: | proxy (WiFi connection count):
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 | 3 | Automatic flow or pressure control without pressure reset: Load dependent supplies of air flow for the demand of all connected rooms. | Demand Management Technologies: Occupant Count prediction: Co-Optimizing IEQ and energy: | electricity: building level: circuit level: battery: HVAC: system level: | thermal: visual: air quality: acoustic: | thermal: solar: wind: air quality: | log: hot water: community level: HVC: zone level: | schedule: setpoint: HVAC: | Occupancy: zone level: | 0 | building characteristics: system characteristics: system chrachtericists (wifi location): | Demand response: tariff: | solar: wind: conventional: | proxy (WiFi connection count):
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 | 4 | Automatic flow or pressure control with pressure reset: Load dependent supplies of air flow for the demand of all connected rooms (for variable air volume systems with VFD). | Demand Management Technologies: Occupant Count prediction: Co-Optimizing IEQ and energy: | electricity: building level: circuit level: battery: HVAC: system level: | thermal: visual: air quality: acoustic: | thermal: solar: wind: air quality: | log: hot water: community level: HVC: zone level: | schedule: setpoint: HVAC: | Occupancy: zone level: | 0 | building characteristics: system characteristics: system chrachtericists (wifi location): | Demand response: tariff: | solar: wind: conventional: | proxy (WiFi connection count):
Ventilation | V-2c | Air temperature control | Heat recovery control: prevention of overheating | 0 | 1 |  | Only in case of mechanical ventilation with heat recovery | 0 | 0 | Without overheating control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ventilation | V-2c | Air temperature control | Heat recovery control: prevention of overheating | 0 | 1 |  | Only in case of mechanical ventilation with heat recovery | 0 | 1 | Modulate or bypass heat recovery based on sensors in air exhaust | ?
Ventilation | V-2c | Air temperature control | Heat recovery control: prevention of overheating | 0 | 1 |  | Only in case of mechanical ventilation with heat recovery | 0 | 2 | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control | ?
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 | 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 | 1 | Constant setpoint: A control loop enables to control the supply air temperature, the setpoint is constant and can only be modified by a manual action | DemandManagement Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 | 2 | Variable set point with outdoor temperature compensation | DemandManagement Technologies: Sensitvity study on weather data: | electricity: building level: circuit level: battery: | thermal: | thermal: visual: solar: wind: onsite/local weather station: | log: hot water: community level: | schedule: setpoint: | 0 | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 | 3 | Variable set point with load dependant compensation. A control loop enables to control the supply air temperature. The setpoint is defined as a function of the loads in the room | DemandManagement Technologies: Sensitvity study on weather data: Co-optimizing IEQ and energy | electricity: building level: circuit level: battery: HVAC: system level: | thermal: visual: air quality: acoustic: | thermal: visual: solar: wind: onsite/local weather station: air quality: | log: hot water: community level: HVAC: zone level: | schedule: setpoint: HVAC: | Occupancy: zone level: | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 | 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 | 1 | Night cooling | Demand Management Technologies: | electricity: building level: circuit level: battery: | thermal: | thermal: | log: hot water: community level: | schedule: setpoint: | 0 | 0 | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 | 2 | Free cooling: air flows modulated during all periods of time to minimize the amount of mechanical cooling | DemandManagement Technologies: Sensitvity study on weather data: | electricity: building level: circuit level: battery: | thermal: | thermal: visual: solar: wind: onsite/local weather station: | log: hot water: community level: | schedule: setpoint: | 0 | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 | 3 | H,x- directed control: The amount of outside air and recirculation air are modulated during all periods of time to minimize the amount of mechanical cooling. Calculation is performed on the basis of temperatures and humidity (enthalpy). | DemandManagement Technologies: Sensitvity study on weather data: Co-optimizing IEQ and energy | electricity: building level: circuit level: battery: HVAC: system level: | thermal: visual: air quality: acoustic: | thermal: visual: solar: wind: onsite/local weather station: air quality: | log: hot water: community level: HVAC: zone level: | schedule: setpoint: HVAC: | Occupancy: zone level: | Drawings: | building characteristics: system characteristics: | Demand response: tariff: | solar: wind: conventional: | 0
Ventilation | V-6 | Feedback - Reporting information | Reporting information regarding IAQ | 1 | 1 |  | Always to be assessed | 1 | 1 | Air quality sensors (e.g. CO2) and real time autonomous monitoring | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Ventilation | V-6 | Feedback - Reporting information | Reporting information regarding IAQ | 1 | 1 |  | Always to be assessed | 1 | 2 | Real time monitoring & historical information of IAQ available to occupants | System level perfomance: | electricity: HVAC: lightning: DHW: EV: | thermal: | 0 | HVAC: plant: system level: | 0 | 0 | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0
Ventilation | V-6 | Feedback - Reporting information | Reporting information regarding IAQ | 1 | 1 |  | Always to be assessed | 1 | 3 | Real time monitoring & historical information of IAQ available to occupants + warning on maintenance needs or occupant actions (e.g. window opening) | System level perfomance: Identifcation and prevention of energy mismanagement | electricity: HVAC: lightning: DHW: EV: fuel: Plug-Ins: | thermal: | thermal: | HVAC: plant: system level: fenestration: | HVAC: setpoint: | Occupancy: Room Level: | Drawings: | building characteristics: system characteristics: | 0 | 0 | 0