## Sheet1
SRIDomain | SRIService | Service group | Smart ready service | PartOfMethodA | PartOfMethodB | part of the custom services list?: 1 - YES; 0 - NO | Preconditions | AffectsMaxScore | Functionality level 0 (as non-smart default) | FunctionalityLevel | FunctionalityDescription | Functionality level 1 | Functionality level 2 | Functionality level 3 | Functionality level 4
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 | No automatic control | 0 | No automatic control
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Individual room control with communication between controllers and to BACS
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Individual room control
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Individual room control with communication and occupancy detection
Cooling | C-1a | Cooling control - demand side | Cooling emission control | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Central automatic control
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Advanced central automatic control with intermittent operation and/or room temperature feedback control
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Advanced central automatic control
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 |  | 4 | Individual room control with communication and occupancy detection
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 | No automatic control | 0 | No automatic control
Cooling | C-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | 0 | 1 |  | Only applicable in case mechanical cooling systems based on TABS are present | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Central automatic control
Cooling | C-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 |  | 3 | Individual room control with communication between controllers and to BACS
Cooling | C-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Demand based control
Cooling | C-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 |  | 4 | Individual room control with communication and occupancy detection
Cooling | C-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Outside temperature compensated control
Cooling | C-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | Constant temperature control | 0 | No automatic control
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 |  | 1 | Central automatic control (e.g. central thermostat) | On off control
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Multi-Stage control
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Variable speed pump control (pump unit (internal) estimations)
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Variable speed pump control (external demand signal)
Cooling | C-1d | Cooling control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable in case mechanical cooling systems with hydronic distribution system are present | 0 | No automatic control | 0 | No automatic control
Cooling | C-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | 0 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | No interlock | 0 | No automatic control
Cooling | C-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | 0 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 |  | 4 | Individual room control with communication and occupancy detection
Cooling | C-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | 0 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 |  | 3 | Individual room control with communication between controllers and to BACS
Cooling | C-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | 0 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Partial interlock (minimising risk of simultanieus heating and cooling e.g. by sliding setpoints)
Cooling | C-1f | Cooling control - demand side | Interlock: avoiding simultaneous heating and cooling in the same room | 0 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Total interlock (control system ensures no simultaneous heating and cooling can take place)
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Cold storage capable of flexible control through grid signals (e.g. DSM)
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Time-scheduled storage operation
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Load prediction based storage operation
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 | Continuous storage operation | 0 | No automatic control
Cooling | C-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 0 | 1 |  | Only applicable in case mechanical cooling systems are present ánd include TES systems | 0 |  | 4 | Individual room control with communication and occupancy detection
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Multi-stage control of cooling production capacity depending on the load or demand (e.g. on/off of several compressors)
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Variable control of cooling production capacity depending on the load AND external signals from grid
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 |  | 4 | Individual room control with communication and occupancy detection
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Variable control of cooling production capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control)
Cooling | C-2a | Control cooling production facilities | Generator control for cooling | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 | On/Off-control of cooling production | 0 | No automatic control
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 | Priorities only based on running times | 0 | No automatic control
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Load prediction based sequencing: the sequence is based on e.g. COP and available power of a device and the predicted required power
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Sequencing based on dynamic priority list, including external signals from grid
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Fixed sequencing based on loads only: e.g. depending on the generators characteristics such as absorption chiller vs. centrifugal chiller
Cooling | C-2b | Control cooling production facilities | Sequencing of different cooling generators | 0 | 1 |  | Only applicable in case multiple mechanical cooling systems are present | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Dynamic priorities based on generator efficiency and characteristics (e.g. availability of free cooling)
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 |  | 0 | No automatic control
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Central or remote reporting of performance evaluation including forecasting and/or benchmarking
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Central or remote reporting of current performance KPIs and historical data
Cooling | C-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 1 | 1 |  | Only applicable in case mechanical cooling systems are present | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage)
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | No automatic control | 0 | No automatic control
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Scheduled operation of cooling system
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Optimized control of cooling system based on local predictions and grid signals (e.g. through model predictive control)
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Self-learning optimal control of cooling system
Cooling | C-4 | Flexibility and grid interaction | Flexibility and grid interaction | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Cooling system capable of flexible control through grid signals (e.g. DSM)
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Combined light/blind/HVAC control
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Motorized operation with manual control
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Predictive blind control (e.g. based on weather forecast)
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Motorized operation with automatic control based on sensor data
Dynamic building envelope | DE-1 | Window control | Window solar shading control | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | No sun shading or only manual operation | 0 | No automatic control
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 1 |  |  | 1 |  | 4 | Individual room control with communication and occupancy detection
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 1 |  |  | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Open/closed detection to shut down heating or cooling systems
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 1 |  |  | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Level 2 + Centralized coordination of operable windows, e.g. to control free natural night cooling
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 1 |  |  | 1 | Manual operation or only fixed windows | 0 | No automatic control
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 1 |  |  | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Level 1 + Automised mechanical window opening based on room sensor data
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Position of each product & fault detection
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Position of each product, fault detection & predictive maintenance
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Position of each product, fault detection, predictive maintenance, real-time sensor data (wind, lux, temperature…)
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 | No reporting | 0 | No automatic control
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance of dynamic building envelope systems | 1 | 1 |  | Only applicable in case movable shades, screens or blinds are present | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Position of each product, fault detection, predictive maintenance, real-time & historical sensor data (wind, lux, temperature…)
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 | Automatic control on / off | 0 | No automatic control
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM)
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Automatic control on / off and scheduled charging enable
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 |  | 4 | Individual room control with communication and occupancy detection
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | 1 | 1 |  | Only applicable in case of DHW storage with electric heating | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Automatic control on / off and scheduled charging enable and multi-sensor storage management
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Automatic control on / off and scheduled charging enable
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 | Automatic control on / off | 0 | No automatic control
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | DHW production system capable of automatic charging control based on external signals (e.g. from district heating grid)
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | 1 | 1 |  | Only applicable in case of DHW storage with non-electrical heat generation | 0 |  | 4 | Individual room control with communication and occupancy detection
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 | Manual selected control of solar energy or heat generation | 0 | No automatic control
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | 0 | 1 |  | Only applicable in case of DHW storage with solar collector | 0 |  | 4 | Individual room control with communication and occupancy detection
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Control according to fixed priority list: e.g. based on rated energy efficiency
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators)
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels)
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid)
Domestic hot water | DHW-2b | Control DHW production facilities | Sequencing in case of different DHW generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | Priorities only based on running time | 0 | No automatic control
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 |  |  | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Performance evaluation including forecasting and/or benchmarking
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 |  |  | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Actual values and historical data
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 |  |  | 1 |  | 0 | No automatic control
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 |  |  | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Indication of actual values (e.g. temperatures, submetering energy usage)
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 1 |  |  | 1 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 |  | Only applicable in case of local energy storage | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 |  | Only applicable in case of local energy storage | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Performance evaluation including forecasting and/or benchmarking
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 |  | Only applicable in case of local energy storage | 0 |  | 0 | No automatic control
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 |  | Only applicable in case of local energy storage | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Actual values and historical data
Electricity | E-11 | Feedback - Reporting information | Reporting information regarding energy storage | 1 | 1 |  | Only applicable in case of local energy storage | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Current state of charge (SOC) data available
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 |  | Always to be assessed | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | real-time feedback or benchmarking on appliance level
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 |  | Always to be assessed | 1 |  | 0 | No automatic control
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 |  | Always to be assessed | 1 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | real-time feedback or benchmarking on appliance level with automated personalized recommendations
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 |  | Always to be assessed | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | real-time feedback or benchmarking on building level
Electricity | E-12 | Feedback - Reporting information | Reporting information regarding electricity consumption | 1 | 1 |  | Always to be assessed | 1 |  | 1 | Central automatic control (e.g. central thermostat) | reporting on current electricity consumption on building level
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 |  | Only applicable in case of local energy generation | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 |  | Only applicable in case of local energy generation | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Actual values and historical data
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 |  | Only applicable in case of local energy generation | 0 |  | 0 | No automatic control
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 |  | Only applicable in case of local energy generation | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Current generation data available
Electricity | E-2 | Feedback - Reporting information | Reporting information regarding local electricity generation | 1 | 1 |  | Only applicable in case of local energy generation | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Performance evaluation including forecasting and/or benchmarking
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 |  | Only applicable in case of local energy generation | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity and possibility to feed back into the grid
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 |  | Only applicable in case of local energy generation | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | On site storage of energy (e.g. electric battery or thermal storage) with controller optimising the use of locally generated electricity
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 |  | Only applicable in case of local energy generation | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | On site storage of energy (e.g. electric battery or thermal storage) with controller based on grid signals
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 |  | Only applicable in case of local energy generation | 0 |  | 0 | No automatic control
Electricity | E-3 | DER - Storage | Storage of (locally generated) electricity | 1 | 1 |  | Only applicable in case of local energy generation | 0 |  | 1 | Central automatic control (e.g. central thermostat) | On site storage of electricity (e.g. electric battery)
Electricity | E-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | 0 | 1 |  | Only applicable in case of local energy generation | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Automated management of local electricity consumption based on current renewable energy availability
Electricity | E-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | 0 | 1 |  | Only applicable in case of local energy generation | 0 |  | 4 | Individual room control with communication and occupancy detection
Electricity | E-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | 0 | 1 |  | Only applicable in case of local energy generation | 0 |  | 0 | No automatic control
Electricity | E-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | 0 | 1 |  | Only applicable in case of local energy generation | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Scheduling electricity consumption (plug loads, white goods, etc.)
Electricity | E-4 | DER- Optimization | Optimizing self-consumption of locally generated electricity | 0 | 1 |  | Only applicable in case of local energy generation | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Automated management of local electricity consumption based on current and predicted energy needs and renewable energy availability
Electricity | E-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | 0 | 1 |  | Only applicable in case of CHP | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | CHP runtime control influenced by the fluctuating availability of RES and grid signals; dynamic charging and runtime control to optimise self-consumption of renewables
Electricity | E-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | 0 | 1 |  | Only applicable in case of CHP | 0 |  | 4 | Individual room control with communication and occupancy detection
Electricity | E-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | 0 | 1 |  | Only applicable in case of CHP | 0 | CHP control based on scheduled runtime management and/or current heat energy demand | 0 | No automatic control
Electricity | E-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | 0 | 1 |  | Only applicable in case of CHP | 0 |  | 3 | Individual room control with communication between controllers and to BACS
Electricity | E-5 | DER - Generation Control | Control of combined heat and power plant (CHP) | 0 | 1 |  | Only applicable in case of CHP | 0 |  | 1 | Central automatic control (e.g. central thermostat) | CHP runtime control influenced by the fluctuating availability of RES; overproduction will be fed into the grid
Electricity | E-8 | DSM- Storage | Support of (micro)grid operation modes | 0 | 1 |  | Only applicable in case of local energy storage | 0 |  | 0 | No automatic control
Electricity | E-8 | DSM- Storage | Support of (micro)grid operation modes | 0 | 1 |  | Only applicable in case of local energy storage | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Automated management of (building-level) electricity consumption based on grid signals
Electricity | E-8 | DSM- Storage | Support of (micro)grid operation modes | 0 | 1 |  | Only applicable in case of local energy storage | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Automated management of (building-level) electricity consumption and supply, with potential to continue limited off-grid operation (island mode)
Electricity | E-8 | DSM- Storage | Support of (micro)grid operation modes | 0 | 1 |  | Only applicable in case of local energy storage | 0 |  | 4 | Individual room control with communication and occupancy detection
Electricity | E-8 | DSM- Storage | Support of (micro)grid operation modes | 0 | 1 |  | Only applicable in case of local energy storage | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Automated management of (building-level) electricity consumption and electricity supply to neighbouring buildings (microgrid) or grid
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | 0-9% of parking spaces has recharging points
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | >50% of parking spaces has recharging point
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 |  | 1 | Central automatic control (e.g. central thermostat) | ducting (or simple power plug) available
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | 10-50% or parking spaces has recharging point
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | 1 | 1 |  | Only to be assessed if parking spots available on site | 0 | not present | 0 | No automatic control
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 |  | 4 | Individual room control with communication and occupancy detection
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 |  | 1 | Central automatic control (e.g. central thermostat) | 1-way controlled charging (e.g. including desired departure time and grid signals for optimization)
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | 2-way controlled charging (e.g. including desired departure time and grid signals for optimization)
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 |  | 3 | Individual room control with communication between controllers and to BACS
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | Not present (uncontrolled charging) | 0 | No automatic control
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 |  | 4 | Individual room control with communication and occupancy detection
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 |  | 3 | Individual room control with communication between controllers and to BACS
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Reporting information on EV charging status to occupant
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Reporting information on EV charging status to occupant AND automatic identification and authorizition of the driver to the charging station (ISO 15118 compliant)
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | 1 | 1 |  | Only to be assessed if EV charging available on site | 0 | No information available | 0 | No automatic control
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Individual room control with communication and occupancy detection
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 | No automatic control | 0 | No automatic control
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Central automatic control (e.g. central thermostat)
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Individual room control (e.g. thermostatic valves, or electronic controller)
Heating | H-1a | Heat control - demand side | Heat emission control | 1 | 1 |  | Triage: not relevant in case of TABS. | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Individual room control with communication between controllers and to BACS
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 |  | 4 | Individual room control with communication and occupancy detection
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Advanced central automatic control with intermittent operation and/or room temperature feedback control
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 | No automatic control | 0 | No automatic control
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Central automatic control
Heating | H-1b | Heat control - demand side | Emission control for TABS (heating mode) | 0 | 1 |  | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Advanced central automatic control
Heating | H-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | 1 | 1 |  | Not applicable in case of individual heaters (e.g. stoves) | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Outside temperature compensated control
Heating | H-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | 1 | 1 |  | Not applicable in case of individual heaters (e.g. stoves) | 0 | No automatic control | 0 | No automatic control
Heating | H-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | 1 | 1 |  | Not applicable in case of individual heaters (e.g. stoves) | 0 |  | 3 | Individual room control with communication between controllers and to BACS
Heating | H-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | 1 | 1 |  | Not applicable in case of individual heaters (e.g. stoves) | 0 |  | 4 | Individual room control with communication and occupancy detection
Heating | H-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | 1 | 1 |  | Not applicable in case of individual heaters (e.g. stoves) | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Demand based control
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 | No automatic control | 0 | No automatic control
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Multi-Stage control
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 |  | 1 | Central automatic control (e.g. central thermostat) | On off control
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Variable speed pump control (external demand signal)
Heating | H-1d | Heat control - demand side | Control of distribution pumps in networks | 0 | 1 |  | Only applicable for hydronic heating systems | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Variable speed pump control (pump unit (internal) estimations)
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Heat storage capable of flexible control through grid signals (e.g. DSM)
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 |  | 4 | Individual room control with communication and occupancy detection
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Load prediction based storage operation
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Time-scheduled storage operation
Heating | H-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 1 |  | Only applicable in case thermal energy storage is present. | 0 | Continuous storage operation | 0 | No automatic control
Heating | H-2a | Control heat production facilities | Heat generator control (all except heat pumps) | 1 | 1 |  | Only applicable in case of combustion heater or district heating | 0 |  | 4 | Individual room control with communication and occupancy detection
Heating | H-2a | Control heat production facilities | Heat generator control (all except heat pumps) | 1 | 1 |  | Only applicable in case of combustion heater or district heating | 0 |  | 3 | Individual room control with communication between controllers and to BACS
Heating | H-2a | Control heat production facilities | Heat generator control (all except heat pumps) | 1 | 1 |  | Only applicable in case of combustion heater or district heating | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Variable temperature control depending on the load (e.g. depending on supply water temperature set point)
Heating | H-2a | Control heat production facilities | Heat generator control (all except heat pumps) | 1 | 1 |  | Only applicable in case of combustion heater or district heating | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Variable temperature control depending on outdoor temperature
Heating | H-2a | Control heat production facilities | Heat generator control (all except heat pumps) | 1 | 1 |  | Only applicable in case of combustion heater or district heating | 0 | Constant temperature control | 0 | No automatic control
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 |  | Only applicable in case of heat pumps | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors)
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 |  | Only applicable in case of heat pumps | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control)
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 |  | Only applicable in case of heat pumps | 0 | On/Off-control of heat generator | 0 | No automatic control
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 |  | Only applicable in case of heat pumps | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Variable control of heat generator capacity depending on the load AND external signals from grid
Heating | H-2b | Control heat production facilities | Heat generator control (for heat pumps) | 1 | 1 |  | Only applicable in case of heat pumps | 0 |  | 4 | Individual room control with communication and occupancy detection
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 | Priorities only based on running time | 0 | No automatic control
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Control according to dynamic priority list (based on current energy efficiency, carbon emissions and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels)
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions and capacity of generators)
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Control according to dynamic priority list (based on current AND predicted load, energy efficiency, carbon emissions, capacity of generators AND external signals from grid)
Heating | H-2d | Control heat production facilities | Sequencing in case of different heat generators | 0 | 1 |  | Only applicable in case of multiple heat generators, mostly restricted to large buildings | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Control according to fixed priority list: e.g. based on rated energy efficiency
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 |  |  | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Central or remote reporting of performance evaluation including forecasting and/or benchmarking
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 |  |  | 1 |  | 0 | No automatic control
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 |  |  | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage)
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 |  |  | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Central or remote reporting of current performance KPIs and historical data
Heating | H-3 | Information to occupants and facility managers | Report information regarding heating system performance | 1 | 1 |  |  | 1 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Central or remote reporting of performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Self-learning optimal control of heating system
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 | No automatic control | 0 | No automatic control
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Optimized control of heating system based on local predictions and grid signals (e.g. through model predictive control)
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Heating system capable of flexible control through grid signals (e.g. DSM)
Heating | H-4 | Flexibility and grid interaction | Flexibility and grid interaction | 0 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Scheduled operation of heating system
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 |  | Always to be assessed | 1 | Manual on/off switch | 0 | No automatic control
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 |  | Always to be assessed | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Automatic detection (manual on / dimmed or auto off)
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 |  | Always to be assessed | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Manual on/off switch + additional sweeping extinction signal
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 |  | Always to be assessed | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Automatic detection (auto on / dimmed or auto off)
Lighting | L-1a | Artificial lighting control | Occupancy control for indoor lighting | 1 | 1 |  | Always to be assessed | 1 |  | 4 | Individual room control with communication and occupancy detection
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Manual (per room / zone)
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Automatic dimming
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Automatic dimming including scene-based light control (during time intervals, dynamic and adapted lighting scenes are set, for example, in terms of illuminance level, different correlated colour temperature (CCT) and the possibility to change the light distribution within the space according to e. g. design, human needs, visual tasks)
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 | Manual (central) | 0 | No automatic control
Lighting | L-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 0 | 1 |  | Always to be assessed | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Automatic switching
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | 1 | 1 |  |  | 1 |  | 4 | Individual room control with communication and occupancy detection
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | 1 | 1 |  |  | 1 |  | 0 | No automatic control
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | 1 | 1 |  |  | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Central or remote reporting of realtime energy use per energy carrier
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | 1 | 1 |  |  | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Central or remote reporting of realtime energy use per energy carrier, combining TBS of at least 2 domains in one interface
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | 1 | 1 |  |  | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Central or remote reporting of realtime energy use per energy carrier, combining TBS of all main domains in one interface
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | 1 | None - No harmonization between grid and TBS; building is operated independently from the grid load | 0 | No automatic control
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Demand side management possible for (some) individual TBS, but not coordinated over various domains
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | 1 |  | 4 | Individual room control with communication and occupancy detection
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Coordinated demand side management of multiple TBS
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | 1 | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | 1 |  | 3 | Individual room control with communication between controllers and to BACS
Monitoring and control | MC-28 | Feedback - Reporting information | Reporting information regarding demand side management performance and operation | 0 | 1 |  |  | 1 |  | 3 | Individual room control with communication between controllers and to BACS
Monitoring and control | MC-28 | Feedback - Reporting information | Reporting information regarding demand side management performance and operation | 0 | 1 |  |  | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Reporting information on currenthistorical and predicted DSM status, including managed energy flows
Monitoring and control | MC-28 | Feedback - Reporting information | Reporting information regarding demand side management performance and operation | 0 | 1 |  |  | 1 |  | 4 | Individual room control with communication and occupancy detection
Monitoring and control | MC-28 | Feedback - Reporting information | Reporting information regarding demand side management performance and operation | 0 | 1 |  |  | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Reporting information on current DSM status, including managed energy flows
Monitoring and control | MC-28 | Feedback - Reporting information | Reporting information regarding demand side management performance and operation | 0 | 1 |  |  | 1 |  | 0 | No automatic control
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Scheduled override of DSM control (and reactivation) by the building user
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Scheduled override of DSM control and reactivation with optimised control
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 | No DSM control | 0 | No automatic control
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Manual override and reactivation of DSM control by the building user
Monitoring and control | MC-29 | Override control | Override of DSM control | 0 | 1 |  |  | 1 |  | 1 | Central automatic control (e.g. central thermostat) | DSM control without the possibility to override this control by the building user (occupant or facility manager)
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | 0 | 1 |  |  | 1 |  | 4 | Individual room control with communication and occupancy detection
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | 0 | 1 |  |  | 1 | Manual setting | 0 | No automatic control
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | 0 | 1 |  |  | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Heating and cooling plant on/off control based on building loads
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | 0 | 1 |  |  | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Runtime setting of heating and cooling plants following a predefined time schedule
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | 0 | 1 |  |  | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Heating and cooling plant on/off control based on predictive control or grid signals
Monitoring and control | MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 1 | 1 |  | Always to be assessed | 1 |  | 4 | Individual room control with communication and occupancy detection
Monitoring and control | MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 1 | 1 |  | Always to be assessed | 1 |  | 0 | No automatic control
Monitoring and control | MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 1 | 1 |  | Always to be assessed | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Single platform that allows automated control & coordination between TBS
Monitoring and control | MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 1 | 1 |  | Always to be assessed | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Single platform that allows manual control of multiple TBS
Monitoring and control | MC-30 | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals | 1 | 1 |  | Always to be assessed | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Single platform that allows automated control & coordination between TBS + optimization of energy flow based on occupancy, weather and grid signals
Monitoring and control | MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 0 | 1 |  |  | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | With central indication of detected faults and alarms for all relevant TBS, including diagnosing functions
Monitoring and control | MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 0 | 1 |  |  | 1 |  | 4 | Individual room control with communication and occupancy detection
Monitoring and control | MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 0 | 1 |  |  | 1 | No central indication of detected faults and alarms | 0 | No automatic control
Monitoring and control | MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 0 | 1 |  |  | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | With central indication of detected faults and alarms for all relevant TBS
Monitoring and control | MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 0 | 1 |  |  | 1 |  | 1 | Central automatic control (e.g. central thermostat) | With central indication of detected faults and alarms for at least 2 relevant TBS
Monitoring and control | MC-9 | TBS interaction control | Occupancy detection: connected services | 0 | 1 |  |  | 1 |  | 3 | Individual room control with communication between controllers and to BACS
Monitoring and control | MC-9 | TBS interaction control | Occupancy detection: connected services | 0 | 1 |  |  | 1 |  | 4 | Individual room control with communication and occupancy detection
Monitoring and control | MC-9 | TBS interaction control | Occupancy detection: connected services | 0 | 1 |  |  | 1 |  | 0 | No automatic control
Monitoring and control | MC-9 | TBS interaction control | Occupancy detection: connected services | 0 | 1 |  |  | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Centralised occupant detection which feeds in to several TBS such as lighting and heating
Monitoring and control | MC-9 | TBS interaction control | Occupancy detection: connected services | 0 | 1 |  |  | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Occupancy detection for individual functions, e.g. lighting
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 | No ventilation system or manual control | 0 | No automatic control
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Clock control
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Occupancy detection control
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers
Ventilation | V-1a | Air flow control | Supply air flow control at the room level | 1 | 1 |  | Always to be assessed | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Central Demand Control based on air quality sensors (CO2, VOC, humidity, ...)
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Multi-stage control: To reduce the auxiliary energy demand of the fan
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 | No automatic control: Continuously supplies of air flow for a maximum load of all rooms | 0 | No automatic control
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Automatic flow or pressure control without pressure reset: Load dependent supplies of air flow for the demand of all connected rooms.
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 |  | 4 | Individual room control with communication and occupancy detection |  |  |  | Automatic flow or pressure control with pressure reset: Load dependent supplies of air flow for the demand of all connected rooms (for variable air volume systems with VFD).
Ventilation | V-1c | Air flow control | Air flow or pressure control at the air handler level | 0 | 1 |  | Only in case of mechanical ventilation | 0 |  | 1 | Central automatic control (e.g. central thermostat) | On off time control: Continuously supplies of air flow for a maximum load of all rooms during nominal occupancy time
Ventilation | V-2c | Air temperature control | Heat recovery control: prevention of overheating | 0 | 1 |  | Only in case of mechanical ventilation with heat recovery | 0 | Without overheating control | 0 | No automatic control
Ventilation | V-2c | Air temperature control | Heat recovery control: prevention of overheating | 0 | 1 |  | Only in case of mechanical ventilation with heat recovery | 0 |  | 3 | Individual room control with communication between controllers and to BACS
Ventilation | V-2c | Air temperature control | Heat recovery control: prevention of overheating | 0 | 1 |  | Only in case of mechanical ventilation with heat recovery | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Modulate or bypass heat recovery based on sensors in air exhaust
Ventilation | V-2c | Air temperature control | Heat recovery control: prevention of overheating | 0 | 1 |  | Only in case of mechanical ventilation with heat recovery | 0 |  | 4 | Individual room control with communication and occupancy detection
Ventilation | V-2c | Air temperature control | Heat recovery control: prevention of overheating | 0 | 1 |  | Only in case of mechanical ventilation with heat recovery | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Variable set point with outdoor temperature compensation
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 | No automatic control | 0 | No automatic control
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Variable set point with load dependant compensation. A control loop enables to control the supply air temperature. The setpoint is defined as a function of the loads in the room
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 |  | 4 | Individual room control with communication and occupancy detection
Ventilation | V-2d | Air temperature control | Supply air temperature control at the air handling unit level | 0 | 1 |  | Only in case of mechanical ventilation which supplies heating | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Constant setpoint: A control loop enables to control the supply air temperature, the setpoint is constant and can only be modified by a manual action
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 |  | 1 | Central automatic control (e.g. central thermostat) | Night cooling
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Free cooling: air flows modulated during all periods of time to minimize the amount of mechanical cooling
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 | No automatic control | 0 | No automatic control
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | H,x- directed control: The amount of outside air and recirculation air are modulated during all periods of time to minimize the amount of mechanical cooling. Calculation is performed on the basis of temperatures and humidity (enthalpy).
Ventilation | V-3 | Free cooling | Free cooling with mechanical ventilation system | 0 | 1 |  | Only in case of mechanical or hybrid ventilation | 0 |  | 4 | Individual room control with communication and occupancy detection
Ventilation | V-6 | Feedback - Reporting information | Reporting information regarding IAQ | 1 | 1 |  | Always to be assessed | 1 |  | 1 | Central automatic control (e.g. central thermostat) | Air quality sensors (e.g. CO2) and real time autonomous monitoring
Ventilation | V-6 | Feedback - Reporting information | Reporting information regarding IAQ | 1 | 1 |  | Always to be assessed | 1 |  | 4 | Individual room control with communication and occupancy detection
Ventilation | V-6 | Feedback - Reporting information | Reporting information regarding IAQ | 1 | 1 |  | Always to be assessed | 1 |  | 0 | No automatic control
Ventilation | V-6 | Feedback - Reporting information | Reporting information regarding IAQ | 1 | 1 |  | Always to be assessed | 1 |  | 3 | Individual room control with communication between controllers and to BACS |  |  | Real time monitoring & historical information of IAQ available to occupants + warning on maintenance needs or occupant actions (e.g. window opening)
Ventilation | V-6 | Feedback - Reporting information | Reporting information regarding IAQ | 1 | 1 |  | Always to be assessed | 1 |  | 2 | Individual room control (e.g. thermostatic valves, or electronic controller) |  | Real time monitoring & historical information of IAQ available to occupants